FETCH / WRITE COMMUNICATION WITH AN 
S7 PLC IN AN MPI SUBNET (ROUTING)

Task

Providing read and write access from an OPC client to an S7 PLC.
The destination PLC is a station in an MPI subnet. The network transition (routing PLC) is represented by an S7-300 PLC. The PLC is connected to Ethernet via an Ethernet CP and, at the same time, is a station in the MPI subnet.

| OPC-Server | OPC server |
| --- | --- |
| OPC-Client | OPC client |
| OPC | OPC |
| ETHERNET | ETHERNET |
| Ethernet-CP | Ethernet CP |
| IP-Adresse = 192.168.3.12 | IP address = 192.168.3.12 |
| Ziel-SPS | Destination PLC |
| Routing-SPS | Routing PLC |
| MPI-BUS | MPI BUS |

Solution

The activity is initiated by the workstation on the Ethernet. The PC uses a FETCH job (Fetch active) to get data and a WRITE job (Write active) to write data.

The S7 PLC remains passive.

On the workstation side, a Fetch active connection and a Write active connection have to be created. When communicating with S7 PLCs, a single connection can be used for both read and write access. This means that only one connection has to be parameterized in the OPC server.

On the PLC side, no connections need to be parameterized.

How to parameterize the connection in the OPC server

● Start the OPC server and select Configuration > Access Path Definitions.

● Select Configuration > New.

● Enter a name for the new connection, select TCP/IP and set the protocol type to S7.

● Click OK to confirm.

● Enter the IP address of the routing PLC as the destination station.

● Select Active under “Connection Establishment.”

● Select the RFC1006 radio button and then click the “ISO on TCP (RFC1006)” button to set the routing TSAPs.

● Select the Routing check box on the right. The following expanded dialog box appears:

● For the destination PLC, enter the S7 subnet ID of the MPI network (in this example, the S7 subnet ID is 10E3-7635).

NOTE

It is essential to make sure that the project from which you read the S7 subnet ID has been loaded to all stations involved.

● For the MPI/Profibus address, specify the MPI address of the destination PLC (in this example, 5).

● Specify the CPU slot in the destination PLC (in this example, 2).

● Select the service. Service “3” is usually used for OPC communication.

● After all settings have been made, click “Generate TSAPs.” The routing TSAPs are displayed in the corresponding fields.

● Click OK to confirm. This takes you back to the dialog box for setting the TCP/IP parameters.
Click OK there, too. The newly parameterized connection is displayed in the connection overview.

● Close the window and exit the OPC server for the settings to take effect.

Parameterizing the connection is now complete. You can now read/write data directly from/to the PLC via an OPC client. Make sure that the name you use for the Access Path is the same as the one you defined as the connection name in the OPC server (in this example, S7-Routing).

Take care to use the correct S7 syntax (a detailed description of the item ID syntax is provided in the OPC server's online help).