FETCH / WRITE COMMUNICATION WITH AN 
S5 PLC WITH CP 1430 VIA ISO (H1)

Task

Providing read and write access from an OPC client to an S5 PLC. 
The S5 PLC has an Ethernet CP 1430. Communication is done via H1.

| PC mit - Step 5 - OPC-Server - OPC-Client | PC with - Step 5 - OPC server - OPC client |
| --- | --- |
| S5 mit Siemens CP 1430 | S5 with Siemens CP 1430 |
| SCHREIBEN | WRITE |
| LESEN | READ |
| Write aktiv | Write active |
| Write passiv | Write passive |
| Fetch aktiv | Fetch active |
| Fetch passiv | Fetch passive |
| ISO (H1) | ISO (H1) |

Solution

To be able to both read data from an S5 PLC and write data to it, a write connection is needed in addition to the read connection. Reading and writing data over a single connection is not possible.

The activity is initiated by the workstation on the Ethernet. The PC uses a FETCH job (Fetch active) to get data and a WRITE job (Write active) to write data.

The S5 PLC remains passive (Fetch passive / Write passive). The connections need to be parameterized on both sides of the communication.

In the OPC server, only a single connection has to be parameterized. The Fetch job and the Write job are specified using the TSAPs. In the S5 PLC, a Write passive connection is created in addition to a Fetch passive connection. The RECEIVE ALL block and the SEND ALL block are also required.

How to parameterize connections in the S5 PLC

● Create two connections in Step 5: one Fetch passive connection and one Write passive connection.

FETCH PASSIVE CONNECTION

● For the Fetch passive connection, select the FETCH job type and enter P for a passive connection establishment.

● Assign the TSAP for the local AG (in this example, FETCHXXX) and the TSAP for the remote station (in this example, OPCSERVV).

WRITE PASSIVE CONNECTION

● For the Write passive connection, select the RECEIVE job type and enter P for a passive connection establishment.

● Assign the TSAP for the local AG (in this example, WRITEXXX) and the TSAP for the remote station (in this example, OPCSERVV).

● The configuration of the connections is now complete. Next, the partner connections are created in the OPC server.

How to parameterize the connection in the OPC server

● Start the OPC server and select Configuration > Access Path Definitions.

● Select Configuration > New.

● Enter a name for the new connection, select H1 and set the protocol type to S5.

● Click OK to confirm.

● Enter the Ethernet address of the CP 1430 as the destination station.

● Select Active under “Connection Establishment.”

● Assign the TSAPs. The local TSAP must correspond to the TSAP you defined as the “Partner TSAP” when parameterizing the connection in the S5 (in this example, OPCSERVV). The remote TSAP for read access must correspond to the TSAP you defined as the local TSAP when configuring the Fetch passive connection in the S5 (in this example, FETCHXXX). The remote TSAP for write access must correspond to the TSAP you defined as the local TSAP when configuring the Write passive connection in the S5 (in this example, WRITEXXX).

● Click OK to close the dialog box. This takes you back to the dialog box for setting the H1 parameters. Click OK there, too.

● The parameterized connection is displayed in the connection overview. Close the window.
You will be asked if you want to save the changes you have made. When you click Yes, you will be prompted to exit the server.

● You can now read data from and write data to the PLC via an OPC client.

● To do this, connect the client and the server, create an OPCGroup and define the OPC items. Make sure that the name you use for the Access Path is the same as the one you defined as the connection name in the OPC server (in this example, S5-Verbindung_H1). Take care to use the correct S5 syntax (a detailed description of the item ID syntax is provided in the OPC server's online help).